## PRO1-Mod
[7 empty] | PRO1-Mod |  |  | Modbus command line - read data |  |  |  |  | Modbus command line - write data
Register Address |  | Contents | Read/Write | Datablocks | HEX response |  |  |  | Remarks | Meter ID | Read | Register address | Register length | CRC code | Meter ID | Write | Register address | Register length | Data length | New value | CRC code | HEX Value | Meter value | Selectable values
[7 empty] | LCD page | Modbus
1000 | 4000 | Serial number | Read | 4 | signed | no need to convert | / | R | By default last 8 digits of serial number | 01 | 03 | 1000 | 0002 | CRC16 Modbus RTU
1010 | 4002 | Meter code | Read | 2 | signed | no need to convert | / | R |  | 01 | 03 | 1010 | 0001 | CRC16 Modbus RTU
1018 | 4003 | Meter ID (Mbus/Modbus) | Read/write | 2 | HEX response | convert to decimal | / | R/W | 001~247 (001 default; 000 broadcast) | 01 | 03 | 1018 | 0001 | CRC16 Modbus RTU | 01 | 06 | 1018 |  |  | 00C7 | CRC16 Modbus RTU | 00C7 | 199
1020 | 4004 | Baud Rate | Read/write | 2 | HEX response | convert to decimal | / | R/W | 9600 (default), 4800, 2400, 1200, 600, 300 | 01 | 03 | 1020 | 0001 | CRC16 Modbus RTU | 01 | 06 | 1020 |  |  | 2580 | CRC16 Modbus RTU | 2580 | 9600 | 9600 | 4800 | 2400 | 1200
1050 | 4005 | Protocol Version | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R | 3.2 = Inepro Modbus protocol version | 01 | 03 | 1050 | 0002 | CRC16 Modbus RTU
1054 | 4007 | Software Version | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R | Shows present software version | 01 | 03 | 1054 | 0002 | CRC16 Modbus RTU
1058 | 4009 | Hardware Version | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R | 1.03, will be updated if hardware modifications are made to the meter | 01 | 03 | 1058 | 0002 | CRC16 Modbus RTU
1060 | 400B | Meter Amps | Read | 2 | HEX response | convert to decimal | / | R | 45A | 01 | 03 | 1060 | 0001 | CRC16 Modbus RTU
1066 | 400D | S0 output rate | Read/write | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P17 | R/W | 10000, 2000, 1000, 100, 10, 1, 0.1, 0.01 | 01 | 03 | 1066 | 0002 | CRC16 Modbus RTU | 01 | 10 | 10 66 | 0002 | 04 | 44FA0000 | CRC16 Modbus RTU | 44FA0000 | 2000 | 10000 | 2000 | 1000 | 100 | 10 | 1 | 0.1 | 0.01
107A | 400F | Combined Code | Read/write | 2 | HEX response | convert to decimal | P26 | R/W | 01, 04, 05, 06, 09 and 10 | 01 | 03 | 107A | 0001 | CRC16 Modbus RTU | 01 | 06 | 10 7A |  |  | 000A | CRC16 Modbus RTU | 000A | 10 | 1 | 4 | 5 | 6 | 9 | 10
1510 | 4010 | LCD cycle time | Read/write | 2 | signed | no need to convert | P15 | R/W | 0~30 (seconds, 10 seconds default) | 01 | 03 | 1510 | 0001 | CRC16 Modbus RTU | 01 | 06 | 15 10 |  |  | 000A | CRC16 Modbus RTU | 000A | 10
2000 | 5000 | Voltage | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P08 | R |  | 01 | 03 | 2000 | 0002 | CRC16 Modbus RTU
2020 | 5008 | Grid Frequency | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P10 | R |  | 01 | 03 | 2020 | 0002 | CRC16 Modbus RTU
2060 | 500A | Current | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P09 | R |  | 01 | 03 | 2060 | 0002 | CRC16 Modbus RTU
2080 | 5012 | Total Active Power | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P11 | R |  | 01 | 03 | 2080 | 0002 | CRC16 Modbus RTU
20A0 | 501A | Total reactive power | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P12 | R |  | 01 | 03 | 20A0 | 0002 | CRC16 Modbus RTU
20C0 | 5022 | Total Apparent Power | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P13 | R |  | 01 | 03 | 20C0 | 0002 | CRC16 Modbus RTU
20E0 | 502A | Power Factor | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P14 | R |  | 01 | 03 | 20E0 | 0002 | CRC16 Modbus RTU
2200 | 6048 | Tariff | Read/write | 2 | signed | no need to convert | / | R/W | 01 (t1 saved), 02 (t2 saved), 11 (t1 not saved), 12 (t2 not saved) | 01 | 03 | 2200 | 0001 | CRC16 Modbus RTU | 01 | 06 | 22 00 |  |  | 0001 | CRC16 Modbus RTU | 0001 | 01 | 01 | 02 | 11 | 12
3000 | 6000 | Total Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P02 | R |  | 01 | 03 | 3000 | 0002 | CRC16 Modbus RTU
3100 | 6002 | T1 Total Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3100 | 0002 | CRC16 Modbus RTU
3200 | 6004 | T2 Total Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3200 | 0002 | CRC16 Modbus RTU
3020 | 600C | Forward Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P04 | R |  | 01 | 03 | 3020 | 0002 | CRC16 Modbus RTU
3120 | 600E | T1 Forward Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3120 | 0002 | CRC16 Modbus RTU
3220 | 6010 | T2 Forward Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3220 | 0002 | CRC16 Modbus RTU
3040 | 6018 | Reverse Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P05 | R |  | 01 | 03 | 3040 | 0002 | CRC16 Modbus RTU
3140 | 601A | T1 Reverse Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3140 | 0002 | CRC16 Modbus RTU
3240 | 601C | T2 Reverse Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3240 | 0002 | CRC16 Modbus RTU
3060 | 6024 | Total Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P03 | R |  | 01 | 03 | 3060 | 0002 | CRC16 Modbus RTU
3160 | 6026 | T1 Total Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3160 | 0002 | CRC16 Modbus RTU
3260 | 6028 | T2 Total Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3260 | 0002 | CRC16 Modbus RTU
3080 | 6030 | Forward Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P06 | R |  | 01 | 03 | 3080 | 0002 | CRC16 Modbus RTU
3180 | 6032 | T1 Forward Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3180 | 0002 | CRC16 Modbus RTU
3280 | 6034 | T2 Forward Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 3280 | 0002 | CRC16 Modbus RTU
30A0 | 603C | Reverse Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P07 | R |  | 01 | 03 | 30A0 | 0002 | CRC16 Modbus RTU
31A0 | 603E | T1 Reverse Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 31A0 | 0002 | CRC16 Modbus RTU
32A0 | 6040 | T2 Reverse Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 32A0 | 0002 | CRC16 Modbus RTU
4000 | 1000 | Serial number | Read | 4 | signed | no need to convert | / | R | By default last 8 digits of serial number | 01 | 03 | 4000 | 0002 | CRC16 Modbus RTU
4002 | 1010 | Meter code | Read | 2 | signed | no need to convert | / | R |  | 01 | 03 | 4002 | 0001 | CRC16 Modbus RTU
4003 | 1018 | Meter ID (Mbus/Modbus) | Read/write | 2 | HEX response | convert to decimal | / | R/W | 001~247 (001 default; 000 broadcast) | 01 | 03 | 4003 | 0001 | CRC16 Modbus RTU | 01 | 06 | 4003 |  |  | 00C7 | CRC16 Modbus RTU | 00C7 | 199
4004 | 1020 | Baud Rate | Read/write | 2 | HEX response | convert to decimal | / | R/W | 9600 (default), 4800, 2400, 1200, 600, 300 | 01 | 03 | 4004 | 0001 | CRC16 Modbus RTU | 01 | 06 | 4004 |  |  | 2580 | CRC16 Modbus RTU | 2580 | 9600 | 9600 | 4800 | 2400 | 1200
4005 | 1050 | Protocol Version | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R | 3.2 = Inepro Modbus protocol version | 01 | 03 | 4005 | 0002 | CRC16 Modbus RTU
4007 | 1054 | Software Version | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R | Shows present software version | 01 | 03 | 4007 | 0002 | CRC16 Modbus RTU
4009 | 1058 | Hardware Version | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R | 1.03, will be updated if hardware modifications are made to the meter | 01 | 03 | 4009 | 0002 | CRC16 Modbus RTU
400B | 1060 | Meter Amps | Read | 2 | HEX response | convert to decimal | / | R | 45A | 01 | 03 | 400B | 0001 | CRC16 Modbus RTU
400C | 1062 | CT rate |  | 2 |  |  |  |  | Only for 3 phase CT meter
400D | 1066 | S0 output rate | Read/write | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P17 | R/W | 10000, 2000, 1000, 100, 10, 1, 0.1, 0.01 | 01 | 03 | 400D | 0002 | CRC16 Modbus RTU | 01 | 10 | 400D | 0002 | 04 | 447A0000 | CRC16 Modbus RTU | 447A0000 | 2000 | 10000 | 2000 | 1000 | 100 | 10 | 1 | 0.1 | 0.01
400F | 107A | Combined Code | Read/write | 2 | HEX response | convert to decimal | / | R/W | 01, 04, 05, 06, 09 and 10 | 01 | 03 | 400F | 0001 | CRC16 Modbus RTU | 01 | 06 | 400F |  |  | 000A | CRC16 Modbus RTU | 000A | 10 | 1 | 4 | 5 | 6 | 9 | 10
4010 | 1510 | LCD cycle time | Read/write | 2 | signed | no need to convert | P15 | R/W | 0~30 (seconds, 10 seconds default) | 01 | 03 | 4010 | 0001 | CRC16 Modbus RTU | 01 | 06 | 4010 |  |  | 000A | CRC16 Modbus RTU | 000A | 10
4011 | 1520 | Parity setting | Read/Write | 2 | signed | no need to convert | / | R/W | 01 (even); 02 (none) | 01 | 03 | 4011 | 0001 | CRC16 Modbus RTU | 01 | 06 | 4011 |  |  | 0001 | CRC16 Modbus RTU | 0001 | 1 | 1 | 2
5000 | 2000 | Voltage | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P08 | R |  | 01 | 03 | 5000 | 0002 | CRC16 Modbus RTU
5002 | 2008 | L1 Voltage |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5004 | 200C | L2 Voltage |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5006 | 2010 | L3 Voltage |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5008 | 2020 | Grid Frequency | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P10 | R |  | 01 | 03 | 5008 | 0002 | CRC16 Modbus RTU
500A | 2060 | Current | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P09 | R |  | 01 | 03 | 500A | 0002 | CRC16 Modbus RTU
500C | 2068 | L1 Current |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
500E | 206C | L2 Current |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5010 | 2070 | L3 Current |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5012 | 2080 | Total Active Power | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P11 | R |  | 01 | 03 | 5012 | 0002 | CRC16 Modbus RTU
5014 | 2088 | L1 Active Power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5016 | 208C | L2 Active Power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5018 | 2090 | L3 Active Power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
501A | 20A0 | Total reactive power | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P12 | R |  | 01 | 03 | 501A | 0002 | CRC16 Modbus RTU
501C | 20A8 | L1 reactive power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
501E | 20AC | L2 reactive power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5020 | 20D0 | L3 reactive power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5022 | 20C0 | Total Apparent Power | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P13 | R |  | 01 | 03 | 5022 | 0002 | CRC16 Modbus RTU
5024 | 20C8 | L1 Apparent Power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5026 | 20CC | L2 Apparent Power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5028 | 20D0 | L3 Apparent Power |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
502A | 20E0 | Power Factor | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P14 | R |  | 01 | 03 | 502A | 0002 | CRC16 Modbus RTU
502C | 20E8 | L1 Power Factor |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
502E | 20EC | L2 Power Factor |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
5030 | 20F0 | L3 Power Factor |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6000 | 3000 | Total Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P02 | R |  | 01 | 03 | 6000 | 0002 | CRC16 Modbus RTU
6002 | 3100 | T1 Total Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 6002 | 0002 | CRC16 Modbus RTU
6004 | 3200 | T2 Total Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 6004 | 0002 | CRC16 Modbus RTU
6006 | 3008 | L1 Total Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6008 | 300C | L2 Total Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
600A | 3010 | L3 Total Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
600C | 3020 | Forward Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P04 | R |  | 01 | 03 | 600C | 0002 | CRC16 Modbus RTU
600E | 3120 | T1 Forward Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 600E | 0002 | CRC16 Modbus RTU
6010 | 3220 | T2 Forward Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 6010 | 0002 | CRC16 Modbus RTU
6012 | 3028 | L1 Forward Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6014 | 302C | L2 Forward Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6016 | 3030 | L3 Forward Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6018 | 3040 | Reverse Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P05 | R |  | 01 | 03 | 6018 | 0002 | CRC16 Modbus RTU
601A | 3140 | T1 Reverse Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 601A | 0002 | CRC16 Modbus RTU
601C | 3240 | T2 Reverse Active Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 601C | 0002 | CRC16 Modbus RTU
601E | 3048 | L1 Reverse Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6020 | 304C | L2 Reverse Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6022 | 3050 | L3 Reverse Active Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6024 | 3060 | Total Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P03 | R |  | 01 | 03 | 6024 | 0002 | CRC16 Modbus RTU
6026 | 3160 | T1 Total Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 6026 | 0002 | CRC16 Modbus RTU
6028 | 3260 | T2 Total Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 6028 | 0002 | CRC16 Modbus RTU
602A | 3068 | L1 Total Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
602C | 306C | L2 Total Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
602E | 3070 | L3 Total Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6030 | 3080 | Forward Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P06 | R |  | 01 | 03 | 6030 | 0002 | CRC16 Modbus RTU
6032 | 3180 | T1 Forward Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 6032 | 0002 | CRC16 Modbus RTU
6034 | 3280 | T2 Forward Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 6034 | 0002 | CRC16 Modbus RTU
6036 | 3088 | L1 Forward Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6038 | 308C | L2 Forward Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
603A | 3090 | L3 Forward Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
603C | 30A0 | Reverse Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | P07 | R |  | 01 | 03 | 603C | 0002 | CRC16 Modbus RTU
603E | 31A0 | T1 Reverse Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 603E | 0002 | CRC16 Modbus RTU
6040 | 32A0 | T2 Reverse Reactive Energy | Read | 4 | Float - Big Endian (ABCD) | convert HEX to Float | / | R |  | 01 | 03 | 6040 | 0002 | CRC16 Modbus RTU
6042 | 30A8 | L1 Reverse Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6044 | 30AC | L2 Reverse Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6046 | 30B0 | L3 Reverse Reactive Energy |  | 4 |  |  |  |  | Only for 3 phase meter (PRO380 series)
6048 | 2200 | Tariff | Read/write | 2 | signed | no need to convert | / | R/W | 01 (t1 saved), 02 (t2 saved), 11 (t1 not saved), 12 (t2 not saved) | 01 | 03 | 6048 | 0001 | CRC16 Modbus RTU | 01 | 06 | 6048 |  |  | 0001 | CRC16 Modbus RTU | 0001 | 01 | 01 | 02 | 11 | 12